"DMTech" Ltd. Pleven

Product passport
Fire conventional panel    FP9000L – 2/4/6/8

Technical Parameters

Product passport

Rev 05:24

- TECHNICAL CHARACTERISTICS

| LINES |  |  |
| --- | --- | --- |
| - Lines: |  |  |
| - Number of lines | 2, 4, 6 or 8 | Optional |
| - Maximum number of fire detectors in a line | 32 |  |
| - Type of the joining line | biconductional |  |
| - Plume maximum resistance | 100 Ω |  |
| - Current thresholds in the lines: |  |  |
| - Interruption | to 4 mA |  |
| - Duty mode | from 4 to 16 mA |  |
| - Fire | from 17 to 70 mA |  |
| - Fire direct /without delay outputs/ | from 40 to 70 mA |  |
| - Short circuit | > 70 mA |  |
| - Lines functional characteristics: |  |  |
| - Verification quantity before entering Fire mode: | 2 |  |
| - Verification and regestrating fault in a earth conductor | yes | selectively |
| OUTPUTS |  |  |
| - Independent relay output in case of fire alarm: |  |  |
| - Quantity | 1 |  |
| - Type | switching | NC / NO |
| - Electrical characteristics | 3А/125V AC, 3A/30V DC |  |

| - Controllable output in case of fire alarm: |  |  |
| --- | --- | --- |
| - Quantity | 2 |  |
| - Type | potentional relay |  |
| - Electrical characteristics | (19-28)V DC/ 0,5A |  |
| - Additional relay outputs (module M9000R 2/4/6/8) in case of fire alarm: |  |  |
| - Quantity | 2/4/6/8 |  |
| - Type | potentional-free | NO |
| - Electrical characteristics | 3А/125V AC, 3A/30V DC |  |
| - Independent relay output in case of failure: |  |  |
| - Quantity | 1 |  |
| - Type | potentional-free, switching | NC / NO |
| - Electrical characteristics | 3А/125V AC, 3A/30V DC |  |
| - Delay outputs: |  |  |
| - Time delay of switching outputs | 0 ÷ 7 minutes |  |
| POWER SUPPLY |  |  |
| - Mains power |  |  |
| - Voltage | (187-252)V AC |  |
| - Frequency | 50/60 Hz |  |
| - Maximum power to mains power | 38W / AC |  |
| - Battery power |  |  |
| - Battery quantity | 2 |  |
| - Type of the battery | Lead, gel |  |
| - Battery rated voltage | 12V DC |  |
| - Rated power C20 | 1.3Ah, 4.5Ah, 5 Ah |  |
| - Charger voltage | 27,6 V DC | temperature compensated |
| Consumption of battery power in standby mode |  |  |
| - Configuration with 2 lines | < 40 mA to 24 V DC |  |
| - Configuration with 4 lines | < 50 mA to 24 V DC |  |
| - Configuration with 6 lines | < 60 mA to 24 V DC |  |
| - Configuration with 8 lines | < 70 mA to 24 V DC |  |
| Time needed in security mode when mains power supply is down with battery 12V/ 5Ah |  |  |
| - Configuration with 2 lines | 120h |  |
| - Configuration with 4 lines | 90h |  |
| - Configuration with 6 lines | 80h |  |
| - Configuration with 8 lines | 72h |  |
| Time needed in security mode when mains power supply is down with battery 12V/1.3Ah |  |  |
| - Configuration with 2 lines | 32h |  |
| Executive devicess powering |  |  |
| - Voltage | (19-28)V DC |  |
| - Maximal current (including the controllable outputs current) | 1А |  |
| Fuses |  |  |
| - Mains power 230V AC | 4,0 A fusible |  |
| - Battery power | 4,0 А fusible |  |
| - Powering external devices | 1,85 А automatic |  |
| - Controllable outputs | 1,1 А automatic |  |

| Functional characteristics |  |
| --- | --- |
| - Control of the lines and controllable outputs for fault conditions (short circuit and interruption) and automatic reset; |  |
| - Ability to delay controllable and general outputs for fire for a period of 0 to 7 minutes after the registration of state Fire with DIP switch; |  |
| - Built-in sounder in case of fire – monotonal, continuous with the possibility of exclusion; |  |
| - Test mode of each (fire alarm) lines; |  |
| - Ability to Disable each of the fire alarm lines; |  |
| - Ability to Disable controllable outputs for fire; |  |
| - Interface for communication with external devices RS485 and networking /optional/; |  |
| - Possibility for GPRS/LAN communication and remote control and monitoring /optional/; |  |
| - Possibility Ability to add module relay M9000R-2/4/6/8. The module expands the outputs of the Panel. |  |
| - Over all size | 310х240х80 mm |
| - Weight without batteries | 1,25 kg |
| - Safety degree | IP30/ EN 60529 |
| The panel meets standarts: |  |
| - EN 54-2:1997 |  |
| - EN 54-2:1997/A1:2006 |  |
| - EN 54-2:1997/AC:1999 |  |
| - EN 54-4:1997 |  |
| - EN 54-4:1997/A1:2002 |  |
| - EN 54-4:1997/A2:2006 |  |
| - EN 54-4:1997AC:1999 |  |
| - EN 50130-4:2011 |  |
| - EN 55022:2006/А1:2007 |  |
| - EN 60950-1:2006/А11:2009 |  |

- WARRANTY

The manufacturer guarantees the product’s conformity with EN 54-2:, EN54-4:. The warranty period is 36 months from the date of sale, provided that:

- the conditions of storage and transport were met;

- the startup has been done by authorized persons;

- The requirements for operation conditioned in this instruction were met;

- Defects are not caused by natural phenomena and accidents of the plug socket

- DELIVEERY COMPOSITION AND COMPLEXITY/SET

| - Fire Station FP 9000L | 1 qty. |
| --- | --- |
| - EOL - resistor 4,7kΩ/0,5W: |  |
| - for configuration with 2 lines /FP9000-2/ | 2 qty. |
| - for configuration with 4 lines /FP9000-4/ | 4 qty. |
| - for configuration with 6 lines /FP9000-6/ | 6 qty. |
| - for configuration with 8 lines /FP9000-8/ | 8 qty. |
| - (EOL) End for controllable output - resistor 4,7kΩ/0,5W; | 2 qty. |
| - Fuse 4,0А; | 2 qty. |
| - Connective bridge for batteries; | 1 qty. |
| - Packaging. | 1 qty. |

1922 – CPR – 1800

DMTech wishes you pleasant work!